{"text_format":"1","workbook":"xlsx","n_sheets":7,"sheets":["Inicio","Mediciones TDD","Cálculos TDD","Mediciones Corriente","Análisis Corriente","Mediciones","Análisis"],"not_rendered":{"charts":0,"images":12,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Inicio","index":0,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Mediciones TDD","index":1,"n_rows":9,"n_cols":12,"rows_kept":9,"cut":false,"hidden":true,"merged":[[4,3,4,5],[3,8,3,9],[3,3,3,5],[7,3,7,5],[7,6,7,8],[7,9,7,11],[7,1,8,1],[7,2,8,2],[7,12,8,12],[7,13,8,13],[7,14,8,14]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Fecha","Hora","Corriente RMS (A)",null,null,"ATHD (%)",null,null,"Corriente Fundamental (A)"]
[null,null,null,"Fase 1","Fase 2","Fase 3","Fase 1","Fase 2","Fase 3","Fase 1","Fase 2","Fase 3"]

{"sheet":"Cálculos TDD","index":2,"n_rows":12,"n_cols":15,"rows_kept":12,"cut":false,"hidden":true,"merged":[[8,11,8,13],[9,11,9,13],[7,8,8,8],[11,11,11,13],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[10,11,10,13],[7,3,8,3],[7,4,8,4],[7,5,8,5],[7,6,8,6],[7,7,8,7]]}
[]
[]
[]
[]
[]
[]
[]
[null,null,null,"Fecha","Hora","Corriente Máx. RMS (A)","ATHD máx (%)","TDD (%)","TDD Límite(%)"]
[null,null,null,null,null,null,null,null,null,null,null,"Corriente de Cortocircuito, Isc (A):",null,null,6490]
[null,null,null,null,null,null,null,null,null,null,null,"Prom. Corriente Fund. (A):",null,null,603.8961392060902]
[null,null,null,null,null,null,null,null,null,null,null,"TDD límite (%):",null,null,5]
[null,null,null,null,null,null,null,null,null,null,null,"Valores inferiores al límite (%)"]

{"sheet":"Mediciones Corriente","index":3,"n_rows":9,"n_cols":13,"rows_kept":9,"cut":false,"hidden":true,"merged":[[7,1,8,1],[7,2,8,2],[7,3,7,5],[7,6,7,12]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Fecha","Hora","Corriente RMS (A)",null,null,"Armónicos Individuales (%)"]
[null,null,null,"Línea 1","Línea 2","Línea 3","Orden 1","Orden 5","Orden 7","Orden 11","Orden 13","Orden 17","Orden 19"]

{"sheet":"Análisis Corriente","index":4,"n_rows":30,"n_cols":16,"rows_kept":30,"cut":false,"hidden":true,"merged":[[13,1,13,2],[14,1,14,2],[15,1,15,2],[16,1,16,2],[7,5,7,6],[8,5,8,6],[9,5,9,6],[10,5,10,6],[11,5,11,6],[12,5,12,6],[7,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[11,1,11,2],[12,1,12,2],[13,5,13,6],[14,5,14,6],[15,5,15,6],[7,9,7,11],[8,9,8,11],[9,9,9,11],[10,9,10,11],[13,9,13,11],[14,9,14,11],[12,9,12,11],[15,9,15,11],[20,8,21,8],[20,9,21,9],[20,10,21,10],[20,3,21,3],[20,4,21,4],[20,5,21,5],[20,6,21,6],[20,7,21,7]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1]
[]
[]
[]
[]
[]
[]
[null,"Transformador",null,null,null,"Promedio Mediciones",null,null,null,"Pérdidas"]
[null,"Potencia Nom. (kVA):",null,1500,null,"Corriente RMS (A):",null,604.26144643828127,null,"Por Corriente en primario (kW):",null,null,0.83792470156106513]
[null,"Tensión Primario (V):",null,13200,null,"Armónico orden 1 (%):",null,100,null,"Por Corriente en secundario (kW):",null,null,2.414204370575562]
[null,"Tensión Secundario (V):",null,228,null,"Armónico orden 5 (%):",null,0.96241163675910868,null,"Por Corrientes Eddy (kW):",null,null,10.907806391795059]
[null,"Relación  Transformación:",null,57.89473684210526,null,"Armónico orden 7 (%):",null,2.5369766177270248]
[null,"Corriente Primario (A):",null,65.607985135184748,null,"Armónico orden 11 (%):",null,1.3703099510603591,null,"Límites"]
[null,"Corriente Secundario (A):",null,3798.3570341422751,null,"Armónico orden 13 (%):",null,0.96258836324089148,null,"Corriente máxima permisible (%):",null,null,96.89516590175019]
[null,"Resistencia Primario(Ω):",null,0.19466666666666665,null,"Armónico orden 17 (%):",null,0.22305600870038059,null,"Corriente máxima permisible (A):",null,null,3680.4243497729558]
[null,"Resistencia Secundario(Ω):",null,1.6733333333333333E-4,null,"Armónico orden 19 (%):",null,8.4774333877107089E-2,null,"Factor de Carga por corriente (%):",null,null,16.418254772049803]
[null,"Pérdidas por carga (kW):",null,15.786]
[]
[]
[]
[null,null,null,"Orden, h","Corriente, Ih (p.u.)","Factor de distribución, fh","h2","Ih (pu)2","fh2","Ih (pu)2h2","fh2h2"]
[]
[null,null,null,1,1,1,1,1,1,1,1]
[null,null,null,5,9.6241163675910863E-3,9.6241163675910863E-3,25,9.2623615856934647E-5,9.2623615856934647E-5,2.3155903964233661E-3,2.3155903964233661E-3]
[null,null,null,7,2.5369766177270249E-2,2.5369766177270249E-2,49,6.4362503588936547E-4,6.4362503588936547E-4,3.1537626758578907E-2,3.1537626758578907E-2]
[null,null,null,11,1.370309951060359E-2,1.370309951060359E-2,121,1.8777493619750435E-4,1.8777493619750435E-4,2.2720767279898028E-2,2.2720767279898028E-2]
[null,null,null,13,9.6258836324089152E-3,9.6258836324089152E-3,169,9.2657635704677854E-5,9.2657635704677854E-5,1.5659140434090557E-2,1.5659140434090557E-2]
[null,null,null,17,2.230560087003806E-3,2.230560087003806E-3,289,4.9753983017344262E-6,4.9753983017344262E-6,1.4378901092012492E-3,1.4378901092012492E-3]
[null,null,null,19,8.4774333877107085E-4,8.4774333877107085E-4,361,7.186687684307226E-7,7.186687684307226E-7,2.5943942540349084E-4,2.5943942540349084E-4]
[null,null,null,null,null,null,"Sumatoria",1.001022375290719,1.001022375290719,1.0739304544035955,1.0739304544035955]

{"sheet":"Mediciones","index":5,"n_rows":9,"n_cols":19,"rows_kept":9,"cut":false,"hidden":true,"merged":[[7,1,8,1],[7,2,8,2],[7,3,7,5],[7,12,7,18],[7,6,7,8],[7,9,7,11]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Fecha","Hora","Corriente RMS (A)",null,null,"Corriente Fundamental (A)",null,null,"ATHD (%)",null,null,"Armónicos Individuales (%)"]
[null,null,null,"Línea 1","Línea 2","Línea 3","Fase 1","Fase 2","Fase 3","Fase 1","Fase 2","Fase 3","Orden 1","Orden 5","Orden 7","Orden 11","Orden 13","Orden 17","Orden 19"]

{"sheet":"Análisis","index":6,"n_rows":31,"n_cols":16,"rows_kept":31,"cut":false,"hidden":true,"merged":[[7,1,7,2],[7,5,7,6],[7,9,7,11],[8,1,8,2],[8,5,8,6],[8,9,8,11],[9,1,9,2],[10,5,10,6],[9,9,9,11],[10,1,10,2],[11,5,11,6],[10,9,10,11],[11,1,11,2],[12,5,12,6],[12,1,12,2],[13,5,13,6],[12,9,12,11],[13,1,13,2],[13,9,13,11],[21,5,22,5],[21,6,22,6],[17,9,17,11],[14,1,14,2],[15,5,15,6],[14,9,14,11],[15,1,15,2],[16,5,16,6],[15,9,15,11],[14,5,14,6],[18,1,18,2],[21,13,22,13],[21,14,22,14],[21,15,22,15],[16,1,16,2],[9,5,9,6],[16,9,16,11],[21,1,22,1],[21,2,22,2],[21,3,22,3],[21,4,22,4],[17,1,17,2],[21,8,22,8],[21,9,22,9],[21,10,22,10],[21,11,22,11],[21,12,22,12]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Transformador",null,null,null,"Promedio Mediciones",null,null,null,"Pérdidas"]
[null,"Potencia Nom. (kVA):",null,1500,null,"Corriente RMS (A):",null,604.26144643828127,null,"Por Corriente en primario (kW):",null,null,0.83792470156106513]
[null,"Tensión Primario (V):",null,13200,null,"Corriente Fundamental (A):",null,603.8961392060902,null,"Por Corriente en secundario (kW):",null,null,2.414204370575562]
[null,"Tensión Secundario (V):",null,228,null,"Armónico orden 1 (%):",null,100,null,"Por Corrientes Eddy (kW):",null,null,10.907806391795059]
[null,"Relación  Transformación:",null,57.89473684210526,null,"Armónico orden 5 (%):",null,0.96241163675910868]
[null,"Corriente Primario (A):",null,65.607985135184748,null,"Armónico orden 7 (%):",null,2.5369766177270248,null,"Límites"]
[null,"Corriente Secundario (A):",null,3798.3570341422751,null,"Armónico orden 11 (%):",null,1.3703099510603591,null,"Corriente máxima permisible (%):",null,null,96.89516590175019]
[null,"Resistencia Primario(Ω):",null,0.19466666666666665,null,"Armónico orden 13 (%):",null,0.96258836324089148,null,"Corriente máxima permisible (A):",null,null,3680.4243497729558]
[null,"Resistencia Secundario(Ω):",null,1.6733333333333333E-4,null,"Armónico orden 17 (%):",null,0.22305600870038059,null,"Factor de Carga por corriente (%):",null,null,16.418254772049803]
[null,"Impedancia (%):",null,6.7,null,"Armónico orden 19 (%):",null,8.4774333877107089E-2,null,"TDD (%):",null,null,12]
[null,"Pérdidas por carga (kW):",null,15.786,null,null,null,null,null,"Valores por debajo de TDD límite (%):"]
[null,"Corriente de Cortocircuito (A):",null,56691.896031974255]
[]
[]
[null,"Fecha","Hora","Corriente Máx. RMS (A)","ATHD máx (%)","TDD (%)","TDD Límite(%)",null,"Orden, h","Corriente, Ih (p.u.)","Factor de distribución, fh","h2","Ih (pu)2","fh2","Ih (pu)2h2","fh2h2"]
[]
[null,null,null,null,null,null,null,null,1,1,1,1,1,1,1,1]
[null,null,null,null,null,null,null,null,5,9.6241163675910863E-3,9.6241163675910863E-3,25,9.2623615856934647E-5,9.2623615856934647E-5,2.3155903964233661E-3,2.3155903964233661E-3]
[null,null,null,null,null,null,null,null,7,2.5369766177270249E-2,2.5369766177270249E-2,49,6.4362503588936547E-4,6.4362503588936547E-4,3.1537626758578907E-2,3.1537626758578907E-2]
[null,null,null,null,null,null,null,null,11,1.370309951060359E-2,1.370309951060359E-2,121,1.8777493619750435E-4,1.8777493619750435E-4,2.2720767279898028E-2,2.2720767279898028E-2]
[null,null,null,null,null,null,null,null,13,9.6258836324089152E-3,9.6258836324089152E-3,169,9.2657635704677854E-5,9.2657635704677854E-5,1.5659140434090557E-2,1.5659140434090557E-2]
[null,null,null,null,null,null,null,null,17,2.230560087003806E-3,2.230560087003806E-3,289,4.9753983017344262E-6,4.9753983017344262E-6,1.4378901092012492E-3,1.4378901092012492E-3]
[null,null,null,null,null,null,null,null,19,8.4774333877107085E-4,8.4774333877107085E-4,361,7.186687684307226E-7,7.186687684307226E-7,2.5943942540349084E-4,2.5943942540349084E-4]
[null,null,null,null,null,null,null,null,null,null,null,"Sumatoria",1.001022375290719,1.001022375290719,1.0739304544035955,1.0739304544035955]